## Defect list
No. | Internal no. | Location | Trade | Item type | Description | Photo / drawing | Responsible | Found on | Status | Costs client / contractor | Visible externally | Remark | Deadline level 1 | Notice received (receipt) | Grace period level 2 | Announcement level 3 | Completion notice | Rectification accepted | Reference date | 2026-09-09 11:57

## Example
No. | Internal no. | Location | Trade | Item type | Description | Photo / drawing | Responsible | Found on | Status | Costs client / contractor | Visible externally | Remark | Deadline level 1 | Notice received (receipt) | Grace period level 2 | Announcement level 3 | Completion notice | Rectification accepted | Reference date | 2026-06-15
M-001 | 2026-041 | Ground floor, group room 1 (0.12) | Drywall | technical defect | Crack in the plasterboard ceiling along the board joint, approx. 1.20 m, joint visible | F-201, F-202 / A-EG-05 rev. b | Drywall A | 2026-05-04 | rectified | contractor | yes | Rectification checked 2026-05-22: crack-free, photo F-260 | 2026-05-18 | 2026-05-05 (e-mail with read receipt) |  |  | 2026-05-20 | 2026-05-22
M-002 | 2026-042 | Ground floor, corridor (0.01), grid line 3 | Screed | technical defect | Hollow spot in the cement screed approx. 0.4 m², tap test hollow, area marked | F-203 / A-EG-05 rev. b | Screed B | 2026-05-04 | rectify | contractor | yes | Grace period expired; tiler waiting for completion notice — prepare announcement of substitute performance (2026-06-15) | 2026-05-18 | 2026-05-06 (registered letter, return receipt) | 2026-06-01
M-003 | 2026-043 | 1st floor, sleeping room 2 (1.08) | Windows | technical defect | Window sash does not close, gasket crushed on the hinge side, draught noticeable | F-210 / window schedule item 14 | Windows C | 2026-05-06 | rectify | contractor | yes | Replacement gasket ordered according to contractor (2026-05-20); substitute performance announced from 2026-06-25, quotation from Windows K on file | 2026-05-20 | 2026-05-07 (e-mail, contractor's reply the same day) | 2026-06-03 | 2026-06-10
M-004 | 2026-044 | Ground floor, children's washroom (0.15) | Plumbing | technical defect | Washbasin 2 not level (6 mm over 60 cm), drain fitting drips | F-215, F-216 / S-EG-02 | Plumbing F | 2026-05-11 | rectified | contractor | yes | Re-installed, leak test 2026-05-20 without findings | 2026-05-25 | 2026-05-11 (handed over on site, countersigned) |  |  | 2026-05-19 | 2026-05-20
M-005 | 2026-045 | 1st floor, corridor (1.01), north wall | Painting | technical defect | Paint patchy, substrate shows through, approx. 8 m² | F-220 / — | Painting D | 2026-05-11 | price reduction | contractor | yes | Second coat no longer possible after furniture delivery; reduction of €380 agreed 2026-05-29 | 2026-05-25 | 2026-05-12 (e-mail, contractor's reply 2026-05-12)
M-006 | 2026-046 | Basement, plant room (U.03) | Electrical | occupational safety | Sub-distribution board UV-2 without cover, live parts touchable, room unlocked | F-225 / E-UG-01 | Electrical E | 2026-05-13 | rectified | contractor | yes | Room locked immediately; cover fitted 2026-05-13 14:30 (F-226), safety coordinator informed 11:10 | 2026-05-13 | 2026-05-13 (by phone 10:15, in writing 11:00 by e-mail) |  |  | 2026-05-13 | 2026-05-14
M-007 | 2026-047 | Ground floor, kitchen (0.20), grid lines 4–5 | Tiling | technical defect | Floor tiles with lippage up to 2 mm, three tiles hollow | F-230, F-231 / A-EG-05 rev. b | Tiling G | 2026-05-19 | to be clarified | open | no | Contractor refers to screed tolerance (M-002); survey with expert agreed for 2026-06-18 — deadline still runs | 2026-06-02 | 2026-05-20 (e-mail with read receipt)
M-008 | 2026-048 | External works, north entrance, ramp | Metalwork | delay | Railing to be installed by 2026-05-15 according to the construction schedule, installation not started; ramp closed | F-235 / construction schedule as of 2026-05-04 | Metalwork H | 2026-05-18 | rectify | contractor | yes | Delay notified; installation according to contractor in week 25 — check contractual penalty under § 11 of the contract | 2026-05-29 | 2026-05-20 (registered letter, return receipt) | 2026-06-12
M-009 | 2026-049 | 1st floor, group room 3 (1.12), ceiling | Roof waterproofing | damage report | Water stain on the ceiling approx. 30 × 40 cm below the roof terrace, cause open (waterproofing or condensation) | F-240 / D-01 | Roof waterproofing K (provisional) | 2026-05-26 | to be clarified | open | yes | Ceiling opened 2026-06-17 with Roof waterproofing K and Drywall A; responsible party final afterwards |  | 2026-05-26 (damage report to both contractors by e-mail, without deadline)
M-010 | 2026-050 | Ground floor, group room 2 (0.13) | Electrical | technical defect | Socket next to the door not working; test report for circuit 12 missing | F-245 / E-EG-03 | Electrical E | 2026-06-02 | rejected |  | yes | Contractor proves: circuit 12 energised only after furniture installation as planned (report 2026-06-03); no defect, number remains | 2026-06-16 | 2026-06-02 (e-mail)
M-011 | 2026-051 | South facade, parapet, grid line 6 | Shell | technical defect | Hairline crack in the fair-faced concrete, width below 0.2 mm, no moisture, course marked | F-250, F-251 / R-03 | Shell J | 2026-06-05 | under observation | open | no | Crack width documented; quarterly check until the end of the warranty period (shell accepted 2025-12-12)
M-012 | 2026-052 | 1st floor, staff WC (1.15) | Painting | technical defect | Paint splash on the wall tile behind the door, approx. 3 mm | F-255 / — | Painting D | 2026-06-05 | irrelevant |  | no | No longer present at the inspection on 2026-06-08; closed instead of deleted — numbering stays unbroken

## Legend
Defect list template: status, responsibility and deadlines, so the chain does not break
Open Experience GmbH · Last updated: 9 September 2026 · Online version with explanations: https://openexperience.de/en/wissen/maengelliste-vorlage/
Disclaimer: Non-binding sample, not legal advice. The list documents — the notice of defects itself is a separate letter that must reach the contractor; deadlines and legal consequences depend on the contract. Legal basis: Germany.
Deadline traffic light (conditional formatting, calculated against the reference date in the header row)
Light red: level 1 deadline passed — no grace period, no completion notice
Red: grace period passed — no announcement of substitute performance, no completion notice
Grey: status from the "closed" group
The columns of the list
Nineteen columns — exactly the data model of Construction Defects, so that a list kept this way can later be taken over without re-mapping. Every column has a reason; anyone who deletes one should know it.
Column | What goes in | Why the column exists
No. | Consecutive number the contractor sees; never changed or reassigned | Unbroken numbers prove that nothing has disappeared
Internal no. | Site supervision's own number, e.g. year and running number | Separates internal processes from external communication
Location | Building, storey, room, grid line — named as in the project structure | Without a location the defect can be neither found nor checked
Trade | Trade by award unit | Assignment to the contractual work and the bill of quantities
Item type | technical defect, delay, damage report, occupational safety, status report | Each type has a different letter and a different deadline logic
Description | Symptom, spot, extent — no cause, no blame | The client has to designate the defect, not explain it (symptom doctrine)
Photo / drawing | Photo numbers and drawing reference with revision | Links the as-built (photo) and the target (drawing) to the entry
Responsible | Contractor (mandatory field); if responsibility is disputed, with the note "provisional" | Without an addressee there is no notice and no deadline
Found on | Date of the finding on site, not of the entry at the desk | Start of the chain and evidential value of the finding
Status | One value from the status model (drop-down list) | One state per defect; the open/closed group drives evaluation and traffic light
Costs client / contractor | Who bears the costs as things stand (contractor, client, open) | Basis for cost estimate, variations and price reduction
Visible externally | yes or no — does the defect appear in the version for contractor and client? | Internal clarifications and assessments stay internal
Remark | Agreements, evidence, reasons — each with a date | The column that is read in a dispute
Deadline level 1 | Date from the notice of defects | Traffic light red if passed without grace period and without completion notice
Notice received (receipt) | Date of receipt with the proof in brackets | Deadlines run from receipt, not from dispatch (§ 130 BGB)
Grace period level 2 | Date from the grace period letter | Prerequisite for level 3; traffic light strong red if passed without announcement
Announcement level 3 | Date of the announcement of substitute performance | From here the cost risk lies with the contractor
Completion notice | Date on which the contractor reports the rectification as complete | Triggers the check — it is not a status
Rectification accepted | Date of the check by site supervision with result | Only now does the status become "rectified"
The status model
Seven states in two groups. A defect has exactly one — and changes it only with a date and a reason in the remark.
Status | Meaning | Group | Who sets it
rectify | Defect found or notified, rectification outstanding | open | Site supervision at the finding
to be clarified | Cause or responsibility disputed; a deadline that has been set still runs | open | Site supervision
under observation | Warranty defect without acute need for action, development is documented | open | Site supervision or client
rectified | Rectification carried out, checked and accepted | closed | Site supervision after its own check — never the contractor
price reduction | Defect remains, remuneration is reduced (§ 13 (6) VOB/B) | closed | Client
irrelevant | Finding without consequence, e.g. trivial or no longer present — number remains | closed | Site supervision with reason
rejected | No defect — the contractor has proven conformity with the contract | closed | Site supervision with evidence in the remark
The contractor's completion notice is deliberately not a status but a date: it triggers the check but does not replace it.
The three escalation levels
Each level is a separate letter with its own legal basis and its own date in the list. The sample letters are in the working aid Notice of defects samples.
Level | Letter | Legal basis | Deadline | If the deadline passes
1 | Notice of defects with deadline for rectification | before acceptance § 4 (7) VOB/B, after acceptance § 13 (5) no. 1 VOB/B; BGB § 634, § 637 | reasonable and stated as a date; starts on receipt | Level 2
2 | Grace period with threat of consequences | before acceptance § 4 (7) sentence 3 with § 8 (3) VOB/B, after acceptance § 13 (5) no. 2 VOB/B | short but feasible; prove receipt again | Level 3
3 | Announcement and execution of substitute performance (before acceptance, withdrawal of the contract for this work) | § 13 (5) no. 2 VOB/B; § 637 BGB, advance payment under subsection 3 | state start and cost estimate | Substitute performance at the contractor's expense
The item types
Not every finding is a technical defect. The type determines which letter follows and whether a deadline runs at all.
Item type | When | What is different
technical defect | Work deviates from the contract, the drawings or the recognised rules of technology | Notice with deadline; three escalation levels
delay | Work not started or completed by the agreed date | Notice of delay referring to the construction schedule instead of a defect description; check contractual penalty
damage report | Damage to finished work or to third-party property, party responsible unknown | Preserve evidence first (photos, date, witnesses), responsible party provisional, deadline only after clarification
occupational safety | Danger to persons | Immediate action, deadline "immediately", report to the safety coordinator; documentation remains even after remedy
status report | Not a defect — a finding on the state of progress for the client | No deadline, no responsible party in the sense of the list; only in the external version
Sources and legal basis
VOB/B (2016 edition), official text of the BMWSB — § 4 (7) (defects before acceptance), § 13 (5) (rectification after acceptance), § 13 (6) (reduction) | https://www.bmwsb.bund.de/SharedDocs/downloads/DE/veroeffentlichungen/bauen/vob-teil-b.pdf?__blob=publicationFile&v=1
§ 634 BGB — Rights of the customer in the case of defects | https://www.gesetze-im-internet.de/bgb/__634.html
§ 637 BGB — Self-help and advance payment | https://www.gesetze-im-internet.de/bgb/__637.html
§ 130 BGB — Effectiveness of a declaration of intent to absent parties (receipt) | https://www.gesetze-im-internet.de/bgb/__130.html
Legal framework: Germany (HOAI, VOB/B, BGB). Deviating contractual agreements take precedence. This working aid is no substitute for legal advice in the individual case.